## Slide 1: Advisories Bulletins & Alert Notices
Nebraska State Fire Marshal Agency – Pipeline Division
February 2026

## Slide 2: REGULATION CHANGES IN 2025
Random Drug Testing Rates for 2026 will continue to be 50%
FAQs published for Type C and Type R Natural Gas Pipelines
NPMS Supplemental Instructions
FAQs Update on Operator Qualification
Executive Order changed marijuana from Schedule I to Schedule III – no changes to DOT employees.
Gas Pipeline Incident Property Damage Threshold increased to $149,700 for federal reporting

## Slide 3
Periodic Updates of Regulatory References to Technical Standards and Miscellaneous Amendments; Additional Technical Amendments; Response to Petition for Reconsideration Amendment 192-137 (July 2025)
§ 192.7 – changed to 2018 version of ASME B31.8 and B31.8S
§ 192.714 – Transmission Line repair criteria referencing B31.8S
§ 192.933 – Actions to address integrity issues that reference ASME B31.8S
REGULATION CHANGES IN 2025

## Slide 4: REGULATION CHANGES IN 2025
Final Rule; Correcting Amendments; Amendment 192-138 - Vacated provision per the order by the court of appeals (January 2025)
(1) Monitoring and mitigation of internal corrosive constituents at § 192.478;
(2) The immediate repair criterion for cracks or crack-like anomalies with predicted failure pressures below 1.25 × maximum allowable operating pressure (MAOP) at §§ 192.714(d)(1)(v)(C) and 192.933(d)(1)(v)(C); and
(3) High-frequency electric resistance welded seams as one of the seam types qualifying for the immediate repair criterion of preferential metal loss on certain seam types at §§ 192.714(d)(1)(iv) and 192.933(d)(1)(iv)
Affected definition of gathering lines §192.9 and Internal Corrosion Direct Assessment §192.927.
Notes: Fiscal note
These items were sent back do to rebuttal from operators on the cost analysis during rule making.

## Slide 5: Limited Enforcement Discretion – 1/2025) Gas Standards Updates (July 2025)
Amendment 192-142 – ASTM A53M-22 Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless Amendment 192-144 – ASTM F2145-23 Standard Specification for Polyamide 11 (PA 11) and Polyamide 12 (PA12) Mechanical Fittings. Amendment 192-145 - ASTM F2600-09(2023), “Standard Specification for Electrofusion Type Polyamide-11 Fittings…. Amendment 192-146 - ASTM F2767-18(2023), “Specification for Electrofusion Type Polyamide-12 Fittings….. Amendment 192-147 - ASTM A578/A578M-17 (2023), “Standard Specification for Straight-Beam Ultrasonic Examination of Rolled Steel Plates for Special Applications,” Amendment 192-148 - ASTM F2817-13(Reapproved 2023), Standard Specification for Poly (Vinyl Chloride) (PVC)…
REGULATION CHANGES IN 2025
Notes: Link, links to a public site
eCfr
Phmsa

## Slide 6: Limited Enforcement Discretion – 1/2025) Gas Standards Updates Cont.
Amendment 192-149 - ASTM F2945-18 (Reapproved 2023 Standard Specification for Polyamide 11 Gas Pressure Pipe, Tubing, and Fittings, approved November 1, 2023 Amendment 192-150 - ASTM F1973-25, Standard Specification for Factory Assembled Anodeless Risers and Transition Fittings in Polyethylene (PE) (PA11) and (PA12) Fuel Gas Distribution Systems Amendment 192-151 - NFPA 70, National Electrical Code (NEC), 2023 edition, effective September 1, 2022; Amendment 192-152 - PPI TR-3, Policies and Procedures for Developing Hydrostatic Design Basis (HDB), Hydrostatic Design Stresses (HDS), Pressure Design Basis (PDB), Strength Design Basis (SDB), Minimum Required Strength (MRS) Ratings, and Categorized Required Strength (CRS) for Thermoplastic Piping Materials or Pipe, May 1, 2024, Amendment 192-153 - PPI TR-4, “PPI HSB Listing of Hydrostatic Design Basis (HDB), Hydrostatic Design Stress (HDS), Strength Design Basis (SDB), Pressure Design Basis (PDB) and Minimum Required Strength (MRS) Ratings For Thermoplastic Piping Materials or Pipe”, updated May 1, 2024
REGULATION CHANGES IN 2025

## Slide 7: Pipeline Safety Class Location Change Requirements “Hot off the Press” - January 12
Authorizes an IM alternative for managing class locations for eligible gas transmission lines segments in Class 3 locations.
Additional initial requirements: 1) integrity assessments and remediation, 2) pressure testing, 3) material records verification, 4) rupture mitigation valves, 5) cathodic protection and coating, and 6) depth of cover. An operator must also provide a notification to PHMSA.
Recurring programmatic requirements: 1) gas quality, 2) close interval surveys, 3) patrolling, 4) leak surveys, 5) line markers, 6) class location studies, 7) shorted casings, and 8) exposed pipe and weld surface examinations.
MAOP may not exceed 72%

## Slide 8: BoLO For PHMSA Press release Old Forms/not updated
PHMSA updated these forms on January 29, 2026
Gas Distribution Incident Report F7100.1
Gas Transmission, Gathering, and UNGS Incident Report F7100.2
Liquefied Natural Gas Facilities Incident Report F7100.3

## Slide 9: What didn’t happen in 2025
Leak Detection Final Rule– advanced review provided January 17, 2025
Cost Recovery for Siting Reviews for LNG Facilities
Gas Distribution Final Rule
Deadline change for annual report.
Change to definition of property damages when reporting an incident.
PHMSA Reauthorization
Notes: Deadline still March 15, add to “deadline change.”

## Slide 10: AMPP Guide 21569-2024, Guidance on Implementing Corrosion Control Methodologies to Align with New PHMSA Regulatory Procedures – provides additional guidance for pipeline operators to assist with the implementation of corrosion control methodology requirements for onshore gas transmission as required in Part 2 of the PHMSA Gas Mega Rule.

## Slide 11: ADB-25-01
The essential elements for this RP include the following:
1) leadership and management commitment (Section 5);
2) stakeholder engagement (Section 6);
3) risk management (Section 7);
4) operational controls (Section 8);
5) incident investigation, evaluation, and lessons learned (Section 9);
6) safety assurance (Section 10);
7) management review and continuous improvement (Section 11);
8) emergency preparedness and response (Section 12);
9) competence, awareness, and training (Section 13);
10) documentation and record keeping (Section 14);
Pipeline Safety Management Systems
API 1173

## Slide 12: NTSB
March 24, 2023 West Reading Pennsylvania
  7 Fatalities
  10 injuries
Retired 1982 Aldyl A service tee with Delrin insert
Degraded tee allowed gas to leak and migrate underground into RM Palmer Company candy Factory
Degradation was aided by elevated ground temperatures from a corroded steam pipe
Advisory Bulletin
ADB-2026-01

## Slide 13: NTSB
Operator was unaware of the nearby steam pipe leading to incomplete integrity Management
Elevated found temperature may increase slow crack growth in susceptible plastic piping materials
Crack growth rate can increase exponentially with small increases in temperature
Elevated Temp also increase rate of decomposition in Delrin insert material
Lack of procedures to report elevated temperatures near assets
ADB 2026-01 Findings

## Slide 14: NTSB
One time inventory of all plastic assets that are experience or are at risk of elevated temperatures
Continue efforts during maintenance and construction projects to identify plastic assets in elevated temperature environments
Evaluate and mitigate risks to deter the degradation of these assets
Address risk associated with Aldyl-A service tees with Delrin inserts including replacing or remediating them.
ADB-2026-01
Encouraged Actions

## Slide 15: NTSB
Related Advisory Bulletins

## Slide 16
ADB-99-02
advised of potential susceptibility of certain plastic pipes installed between 1960 and the early 1980s to premature failure due to brittle-like cracking

## Slide 17: ADB-02-07
Provided recommendations for identifying and managing brittle-like cracking for certain vintage polyethylene pipe and noted the susceptibility of older plastic pipe to premature failure by brittle-like cracking. Susceptible materials included ‘‘low-ductile inner wall ‘Aldyl A’ polyethylene piping manufactured by Dupont Company before 1973’’ and polyethylene gas pipe designated PE 3306. It also identified other environmental, installation, and service conditions that could contribute to premature failure of polyethylene pipe such as inadequate support and backfill during installation; rock impingement; nearby excavation; service temperatures; and higher ground temperatures.

## Slide 18: ADB-07-01
updated the list of pipe material susceptible to brittle-like cracking to include Delrin insert tap tees and Plexco service tee Celcon (polyacetal) caps.

## Slide 19: ADB-2012-03
Alerted operators using Driscopipe 8000 highdensity polyethylene (HDPE) pipe of the potential for material degradation. At the time of the ADB’s publication, the root cause of the material degradation had not been determined. The manufacturer has since investigated and determined the root cause of degradation to be thermal oxidation for both Driscopipe 7000 and 8000 HDPE piping. The manufacturer also concluded that the potential for thermal oxidation increases with increased temperature of the pipe and with increased time at the elevated temperature conditions.17 Together, these advisories alerted operators to the risk of premature, brittle-like cracking and outline contributing environmental and installation factors.

## Slide 20: ADB-2020-02
Reminded operators of their obligation to comply with gas DIMP regulations, including requirements for an operator to demonstrate knowledge of their system and to identify the characteristics of its pipeline design, operation, and environment when assessing applicable threats and risks.19 The ADB also provided guidance in identifying threats, ranking risk, and determining and implementing measures designed to reduce the risk of failure. Specifically, PHMSA advised that ‘‘[a] potential accident of relatively low likelihood but one that would produce significant consequences may be a higher risk than an accident with somewhat greater likelihood, but one that is not expected to produce major consequences.’’ 20 PHMSA has also provided ongoing guidance through its Distribution Integrity Management Frequently Asked Questions (FAQs) stating that brittle-like cracking of Aldyl A piping should be considered a threat in a DIMP under the category of ‘‘material,’’ even if operators have not experienced any issues or leaks
from Aldyl A piping.

## Slide 21: Related NTSB Recommendations to the states
Require the installation of natural gas alarms that meet the specifications of National Fire Protection Association 715 in businesses, residences, and other buildings where people congregate that could be affected by a natural gas leak. (P-25-5)

## Slide 22: Cast IRon
Considerations
Graphitization
Ground Movement
History
Proximity to Exposures
Notes: (a) General. A graphitized cast iron pipe is one in which iron has been converted to corrosion products leaving graphite, with the pipe seemingly left intact. This is evidenced by the pipe being soft and able to be shaved away with a knife or other type of blade.
Repair. Where inspection indicates that general or localized graphitization has proceeded to the extent that fracture or leakage may result, the operator should determine the extent of graphitization by exposing additional pipe. The pipe may be repaired by a clamp or sleeve, provided that the repair clamp or sleeve will cover the graphitized area and the ends of the repair clamp or sleeve are over sound, non-graphitized pipe.
(a) Water line leaks.
(b) Sewer line failures.
(c) Excavations for construction work.
Excavations for repair or replacement of other underground facilities.
(1) An inspection indicates a graphitized or soft condition is adjacent to a building, sewer, manhole, or duct, or in an area subject to heavy vehicular traffic.

## Slide 23: Directional Drilling Procedures
Ourselves
Contractors
Who can we Manage?
Notes: Utilize procedures in damage prevention program to aid in operator and contractor damage reduction.
Considerations –
Require potholing
Offer potholing for crossing
If parallelling verify location and depth every x amount of feet.

## Slide 24: Bridgeport, Alabama January 22, 1999
Excavator wrapped black tape over the line at the excavations site
Utility board operated both the gas and water system
Could hear gas blowing and was unsure of direction
Supervisor “was hoping” line was pulled off at the main and believed situation was safe
Gas was bubbling up from the water in the ditch
No barhole testing performed or checking for accumulation in buildings
Excavation Damage with multiple leaks
3 fatalities
6 injuries 5 serious
3 Structures Destroyed
Notes: January 22, 1999 trenching with a backhoe and operator damaged a ¾” steel service and adjacent 1” water line. 2 leaks were caused, one where the equipment contacted and pulled the line, the other at a joint near the meter near the structure. Gas migrated and explosion occurred at 406 Alabama and also destroyed 404 and 408 Alabama. Significant damage to other buildings. Three fatalities 5 serious injuries and one minor injury.
Excavator wrapped black tape over the line at the excavations site
Utility board operated both the gas and water system
Could hear gas blowing and was unsure of direction
Supervisor “was hopin
g” line was pulled off at the main and believed situation was safe
Gas was bubbling up from the water in the ditch
No barhole testing performed or accumulation in buildings

## Slide 25
Review Emergency Procedures to determine if procedures prompt the appropriate actions for gas leaks caused by excavation damage near buildings and where the possibility of multiple leaks and underground migration.
Notes: Regulators also have a responsibility to review these procedures for adequacy

## Slide 26: Silver Spring, MD August 10, 2016
Require that all new service regulators be installed outside occupied structures. (P-19-001)
• Require existing interior service regulators be relocated outside occupied structures whenever the gas service line, meter, or regulator is replaced. In addition, multifamily structures should be prioritized over single-family dwellings. (P-19-002)
14 unit apartment building, unincorporated community
7 dead 65 transported plus 3 firefighters
1 Million in damages
Notes: 2 service regulators piped into a common vent line that was broken allowing gas to vent into a meter room
6 service calls over the previous 5 years
Twice to turn on gas service
Believed that the vent line was left open due to inadequate procedures

## Slide 27: July 2, 2017 Millersville, PA
Over torque resulting in broken/malfunctioning nylon bolts on Permalock mechanical tapping tee assembly by Honeywell
Gas leak resulting in explosion of 3 story brick building
Single fatality and 3 injured.
Review and strictly adhere to installation instructions to prevent over torque and component malfunction.
Conduct leak surveys of installations when appropriate.

## Slide 28: !!!...Thank you…!!! Presenters operators contractors vendors & stakeholders -Regards, nsfm